## FL5000 Flame Detector
FL5000 Flame Detector Technical Specification Summary Sheet
Manufacturer | MSA
Model | General Monitors® FL5000
Instrument Description | The FL5000 is a Multi-Spectral Infrared (MSIR) Flame Detector with high false alarm immunity and a large field of view. Additionally, it offers an easy upgrade solution from the FL4000H, Bluetooth, and a heater. With 22 FM approved fuels listed, it is ready to cover your flame detection needs.
Mechanical
Housing material | Polyester TGIC Powder Coated 316 Stainless Steel
Weight, FL5000 Housing Only | 7.6 lbs (3.447 kg), (w/ mount bracket): 9.125lbs (4.139 kg)
Conduit entries & thread options | 4 x 3/4" NPT or M25
Enclosure rating | Class I, Div. 1, Groups B, C, D T4 Class II/III, Div. 1/2, Groups E, F, G Class I, Div. 2, Groups A, B, C, D T4 (-40°C ≤ Ta ≤ +80°C) Type 6P, IP66/67 Class I, Zone 1, AEx db IIC T4 Gb Zone 21, AEx tb IIIC T135°C Db Ex db IIC T4 Gb Ex tb IIIC T135C Db -55°C ≤ Ta ≤ +80°C, IP66/67
Upgradeable Design from FL4000H | Yes
Electrical
Nominal supply voltage | 24 VDC (5.7 W with Heater 'OFF', 8.9 W with Heater 'ON')
Range | 20 to 32 VDC
Maximum power consumption | 6.2 W (heater ‘OFF’) 9.7 W (heater ‘ON’)
Relay Contact Ratings | 8 A @ 24 VDC, Resistive MAX
Baud Rate | 2400, 4800, 9600, 19200, and 38400 Baud
Analog Signal Options | HART (1.25 mA) HART (3.5 mA) HART Disabled/Off
Output signal range: 1.25 – 20 mA 3.5 – 20 mA 0 to 20 mA
FAULT signal: 1.25 mA 3.5 mA 0 to 0.2 mA
COPM fault signal: 2.0 ± 0.2 mA 3.5 mA 2.0 ± 0.2 mA
Ready signal: 4.05 ± 0.2 mA 4.05 ± 0.2 mA 4.3 ± 0.2 mA
INSTANT ALARM signal: 16.0 ± 0.2 mA 16.0 ± 0.2 mA 16.0 ± 0.2 mA
SUSTAINED ALARM signal: 20.0 ± 0.2 mA 20.0 ± 0.2 mA 20.0 ± 0.2 mA
Bluetooth load: 3.0 mA 3.0 mA 3.0 mA
HART Communication Option | HART Rev 7
Modbus RS-485 | Yes
Diagnostics
Status Indicator | Four LEDs indicate status, fault conditions
Instrument Status LED Display | Power On/Normal=Green, Fault= Yellow, Alarm= Red, Blue = Bluetooth
Status LED indication | Yes
Wireless Connectivity | Bluetooth Low Energy (BLE)
Environmental
Operating Temperature | *-40°F to 176°F (-40°C to 80°C) - FM3260 & ULC-ORD-C386 *-67°F to 176°F (-55°C to 80°C) - EN54-10 & DNV-CG-0339
Humidity | 0% to 95% RH, non-condensing
Accessories
Test Lamp with Charger - PN TL105-1001 | Yes
Mounting Bracket - PN 71370-1 | Yes
Rain Guard - PN 712006-1 | Yes
Air Curtain - PN 712880-1 | Yes
3/4" NPT Plug - PN 10177576 | Yes
M25 Plug - PN 10203507 | Yes
Thread Adapter - PN 914-196 | Yes
FL4000H Upgrade Kit - PN 10242703 | Yes
Approvals
Factory Mutual (FM) | Yes
CSA | Yes
ATEX/IECEx | Yes
SIL Certification | SIL 2 & 3 Suitable